## Slide 1
Energy Cost Minimization for Small Building with Renewable Energy Sources Based on Prediction Control
Viktor Ten, Zhandos Yessenbayev, Akmaral Shamshimova, Albina Khakimova
Nazarbayev University, NLA
Almaty, 2015
Посольство Республики Корея в Казахстане
Корейское научно-техническое общество «КАХАК»
Казахский национальный университет им. аль-Фараби

## Slide 2
Renewable Energy Test Site at Nazarbayev University, Astana, Kazakhstan

## Slide 3
Control Plant is a combination of two subsystems:

## Slide 4
Objectives and Implementation
Objective – simultaneously satisfied requirements:
maintain the indoor temperature within a comfort zone;
satisfy demand of electrical power from the electrical loads;
minimize overall consumption of energy sourced by grid;
minimize cost of consumed energy.
Implementation algorithm:
obtain a control oriented state-space model which captures main thermal and electric dynamics, activation of the pumps, heating coil and the connection to the grid  system identification;
define operating constraints including logic constraints and limits on the system variables;
design an controller with preview capabilities on desired room temperature, electricity tariff, outside temperature and solar radiation:
Model Predictive Control (MPC),
Control based on Genetic Algorithm.

## Slide 5
Electrical subsystem
Load can be powered either directly by the grid (ugrid=1) or by the battery bank through an invertor (ugrid=0)
Current generated by PV is assumed to be linearly proportional to solar radiation(coefficient obtained by a linear regression):
Q = 800 Ah
Sample at Ts = 10mins

## Slide 6
Grey-box model:
Discrete-time model structure:
Model is nonlinear  convert to a linear system with hybrid dynamics
4 possible combinations of  4 linear
models combined into a switched linear system
The coefficients of matrices A, B and D were determined using a simple linear regression
State vector:
Disturbance input vector:
Thermal Subsystem

## Slide 7
Controller
PV
Battery pack
Thermal model
SoC
Troom
Resistor On/Off
Pumps On/Off
Grid/Battery
βforecast
€
System
Tamb, Ee
Iload
ipv
Uload
Overall system
Discrete states: x(k) = temperatures, state of charge at time k
Discrete output: y(k) = temperature tracking error at time k
Discrete disturbances: d(k) = outside T, solar radiation, tariff at time k
Binary inputs: u(k)= grid/battery switch, pumps on/off, resistor on/off at time k

## Slide 8
Optimal control problem: minimize the cost function – analogous to the overall electricity cost
The input sequence for optimal behaviour
Stabilization problem: maintain all states of the system within the required ranges:
Control Task

## Slide 9
Model Predictive Control (MPC)
Theory behind MPC
MPC is based on iterative, finite-horizon optimization of a plant model.
At time t the current plant state is sampled and a cost minimizing control strategy is computed (via a numerical minimization algorithm) for a relatively short time horizon in the future: [t,t+T].
Specifically, an online or on-the-fly calculation is used to explore state trajectories that emanate from the current state and find (via the solution of Euler–Lagrange equations) a cost-minimizing control strategy until time t+T.
Only the first step of the control strategy is implemented, then the plant state is sampled again and the calculations are repeated starting from the new current state, yielding a new control and new predicted state path. The prediction horizon keeps being shifted forward and for this reason MPC is also called receding horizon control.

## Slide 10
Model Predictive Control (MPC)
Principles of MPC:
Model Predictive Control (MPC) is a multivariable control algorithm that uses:
an internal dynamic model of the process
a history of past control moves and
an optimization cost function J over the receding prediction horizon, to calculate the optimum control moves.
An example of a non-linear cost function for optimization is given by:
without violating constraints (low/high limits)
With:
xi = i-th controlled variable (e.g. measured temperature),
ri = i-th reference variable (e.g. required temperature),
ui = i-th manipulated variable (e.g. control valve),
wxi = weighting coefficient reflecting the relative importance of xi,
wui = weighting coefficient penalizing relative big changes in ui, etc.

## Slide 11
Genetic Algorithm (GA)
GA – a heuristic evolutionary optimization algorithm
Representation:
Population initialization:
Crossover:
Mutation:
Selection:
  parents selection
  best individuals selection

## Slide 12
Genetic Algorithm (GA)
Selection
Crossover
Mutation
Renew population
Start
Initial population
Fitness evaluation
Stop?
Final population
Finish
Yes
No
Notes:
Population generation must respect the constraints
Elitism might be used in population generation
General procedure of GA

## Slide 13
Genetic Algorithm (GA)
GA specifications in MATLAB
Parameter | Value
Representation | Binary vector u(k) = [ugrid(k), ures(k), uc(k), ur(k)] stacked together for each time k, T = 2880
Fitness function | Energy cost as described above
Constraints | Non-linear constraints described as above
Initialization | Uniformly
Selection function | Stochastic uniform (walk through random intervals)
Crossover function | Scattered algorithm (mask random binary vector)
Mutation function | Gaussian distribution (add a random number with mean 0)
Generation size | 500 chromosomes
Elite count | 2
Termination criteria | Stall generation (=20) + Function tolerance (=1010)

## Slide 14
MPC Simulation results
Controller: Ts=30 mins, Prediction: 8 hours; N=16;
Simulation: 5 days; Ts=10 mins Economy: ~ 3 EUR (European Tariffs)

## Slide 17
GA Apply Simulation Results
Controller: Ts=30 mins, Prediction: 8 hours; N=16;
Simulation: 5 days; Ts=10 mins Economy: ~3 Euro

## Slide 20
Thank you for attention!
Acknowledgements
Organizers of the seminar and ‘Kahak’ staff:
Пак Иван Тимофеевич, проф., почетный президент НТО «Кахак»,
Мун Григорий Алексеевич, проф., президент НТО «Кахак»,
Ю Валентина Константиновна, проф., вице-президент НТО «Кахак»,
Югай Ольга, зам. отв. секретаря журнала «Известия НТО Кахак», и др.
Research Team and Administration of NLA at NU:
Prof. Alex Tikhonov – Director for Center for Energy Research,
Dr. Zhandos Yessenbayev – Senior Researcher,
Akmaral Shamshimova – Junior Researcher,
Albina Khakimova – Junior Researcher,
Dana Sharipova – Research Assistant,
Aliya Kusatayeva – Junior Researcher, and others.